### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 5th October 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Miss Emma McDonald and Mr Ed Hutton (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – All Hoppers full with complete covering of algae - requires draining/over-pumping. Tank 1B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 3 full and Hopper 2 approx. 75% full with complete covering of algae - requires draining/over-pumping. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 75% full & Hoppers 2 & 3 approx. 25% full with complete covering of algae - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 60% full with complete covering of algae - requires draining/over-pumping. Tank 3A – Tank empty – Approx. 75% of tank covered by thick covering of grit and sludge – requires further flushing – All Hoppers approx. 75% full with thick crust of sludge - requires draining/over-pumping. Tank 3B – Tank backfilling – approx. 60% of Tank and all Hoppers covered – requires draining/over-pumping. – Approx. 20% of remainder of tank covered by grit and sludge – requires further flushing. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty and flushed clean – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 20% of tank covered by thick covering of grit and sludge – requires further flushing – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 7A – Tank in use – no Amajets in use. Tank 7B – Tank empty – recently returned – Approx. 75% of tank covered by thick covering of grit and sludge – requires further flushing – All Hoppers containing quantity of grit - requires flushing/removal. Tank 8A – Tank backfilling – approx. 60% of Tank and all Hoppers covered – requires draining/over-pumping. Remainder of Tank clean. Tank 8B – Tank backfilling – approx. 40% of Tank and all Hoppers covered – requires draining/over-pumping. – remainder of tank completely covered by grit and sludge – requires further flushing. Feed Channel - The level of effluent in both feed channels was approximately 30% capacity. |  |
| Complaints The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .004; ppm; 15:31. Monitor 2; .001; ppm; 15:31. Monitor 3; .004; ppm; 15:31. Monitor 4; .004; ppm; 15:31. Monitor 5; .000; ppm; 15:31. Monitor 6; .005; ppm; 15:31. Monitor 7; .000; ppm; 15:31. Monitor 8; .006; ppm; 15:31. Monitor 9; .003; ppm; 15:31. Monitor 10; .004; ppm; 15:33. Monitor 11; .005; ppm; 15:33. Monitor 12; .004; ppm; 15:33. Monitor 13; .004; ppm; 15:33. Wind Speed; 2.1; mph; 15:33. Wind Direction; 228°; 15:33. |  |
| Odour Log (Thames): Wednesday 28th September 2022: AM – Warm – Cloudy with Sunny spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cold – Clear Night. All OMU’s in use. Observations/Complaints: “No issues.” Operational Issues/Causes ”PAS Stream Sludge spill.” Actions: No data. Thursday 29th September 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data PM – Cold – Clear Night. All OMU’s in use. Observations/Complaints: “OM6 0.023 21:34-22:06, OM8 0.016 21:08-21:23, 0.029 19:38-20:26. OM4 0.025 19:40-20:43, OM10 0.016 19:04-19:20.” Operational Issues/Causes: ”Some odour from PAS but no obvious source. OCU11 vent stack PPM high.” Actions: No data. Friday 30th September 2022: AM – Cool – Rain with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Rain. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. Saturday 1st October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Patchy Rain. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. Sunday 2nd October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. Monday 3rd October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. Tuesday 4th October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: ”No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes No data. Actions: No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 30/09/22; 79; 183; 412; 674; 936; 1610. 03/10/22; 98; 450 (TW figure 650 ?); 412; 960; 1088 (TW figure 1416 ?); 2048 (TW figure 2576 ?). 05/10/22; 79; 267; 328; 674; 1088; 1762. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. Digester 6 - In use – seal level approx. 6” below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 7 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 8 - In use – seal level approx. 4ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 9 - In use – seal level approx. 3ft below coping stones – Seal weak and bubbling. Digester 10 - In use – seal level approx. 4ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 11 - In use – seal level approx. 3ft below coping stones – Seal weak and bubbling. Digester 12 - In use – seal level approx. 3ft below coping stones – Seal weak and bubbling – ongoing spill requiring clean-up and anti-foam. Digester 13 - In use – seal level approx. 2ft below coping stones - Seal weak and bubbling – quantity of rag/litter and other extraneous matter observed within seal . Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 2ft below coping stones - Seal weak and bubbling. Digester 18 – In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. Digester 19 – In use – seal level approx. 18” below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 20 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. |  |
| GENERAL Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge One Hundred and Five (105) Imports in preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. Tanks 71 & 73 currently out of service and undergoing complete overhaul – Contractors on site. FST’s 61-64 drained down – quantity of sludge at bottom of each – significant localised odour – requires removal. East Side Raw Sludge Screen House Doors open at time of inspection – Contractors on site undertaking maintenance. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E No issues. Pasteurisation Plant No Data. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) covered with tarpaulin & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. |  |

Odour Control Unit (OCU) performance monitoring – 03/10/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.11 0.09 0.07 | 0.2 | Yes |
| East OCU | 0.219 0.217 0.214 | 0.05 | No |
| West inlet OCU | 0.051 0.055 0.059 | 0.05 | No |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.118 0.112 0.109 | 0.6 | Yes |
| Transfer PS inlet | 5.70 5.21 6.82 | Unknown | Unknown |
| Transfer PS outlet | 0.024 0.018 0.016 | 0.5 | Yes |
| New West inlet (OCU11) | 0.602 0.616 0.615 | 0.5 | No |
| Pasteurisation Plant (OCU12) | 2.278 2.293 2.301 | 0.5 | No |
| GBT Plant OCU Outlet | 0.011 0.009 0.007 | Unknown | Unknown |